## Slide 1
EPRI (www.epri.com) rules
Electric Power Research Institute
Action levels (in a case of deviation from operating values) :
1, determine the cause, remedy, not necessary to decrease the power
2, remedy (even without knowledge about cause), partly decrease of the power
3, shutdown
Main aims
Primary loop
decrease the induced activity,
corrosion
Secondary loop
purity
corrosion errosion
Third loop (cooling loop)
reduction of the presence of microorganisms
contact with concrete and with nature (law standards)

## Slide 2
Quantity | Frequency of meas. | Value
H3BO3 | cont. or 1*D | 0 – 8 g/kg
H2 | cont. or 2*W | 30-60 Nml/kg
O2 | If failure to comply with standards of H2 | < 10μg/kg
Cl- | cont. or 2*D | <0.1 mg/kg
Cl- + F- | 1*W | <0.1 mg/kg
NH3 | 1*S | > 5 mg/l
K+ | 2*W | 2 – 16.5 mg/kg
pH (25oC) | cont. or 1*D | > 6
conductivity | kont. | No standard
Na+ + Li+ | 1*W | 1*10-4 mol/kg
oil | 1*W | < 0.05 mg/kg
Corr. products (odp. Fe) | 1*W | 0,2 mg/kg
Activity J (or summary ) | cont. or 1*D | 3,7*107 Bq/kg
N2H4 – hydrazin hydrate [*] |  | 20-30 mg/kg
[*] into solutions which are added without degassing (do roztoků, které se doplňují bez odplynění)
Primary loop

## Slide 3
Parametr | Unit | Normal value | 1.A.L. | 2.A.L. | 3.A.L.
K, Li, Na (K) | mmol/l | 0,010 - 0,350 | > 0,350 | - | -
Hydrogen | Nml/l | 20 – 50 | < 20; > 50 | < 5; > 50 | -
Cl | mg/l | 0,010 - 0,100 | - | > 0,100 | > 0,150
F | mg/l | 0,010 - 0,100 | - | > 0,100 | > 0,150
oxygen | mg/l | <0,005 | > 0,005 | > 0,010 | > 0,100
pH300 | - | 7,0 - 7,2 | 6,9-7,0; 7,2-7,5 | < 6,9; > 7,5 | -
Parametr | Unit | Normal value
H3BO3 | g/kg | After reactivity of AZ
NH4 | mg/l | > 5
Corrosion products (Fe) | mg /l | less then 0,200
Sum of activity | Bq/l | Less then 3,7x108
SO4 | mg/l | Less then 0,100
SiO2 | mg/l | Less than 0,200
pH25 | - | 5,7 - 10,2
Optical transmittance | % | > 95
NEL | mg/l | < 0,100
Diagnostic parameters
Controlling parameters

## Slide 4
Value | Units | Water supply | PG blowdown | SG condensate
pH(25oC) |  | 7,5-8,5 |  | 
conductivity cat. | μS/cm | <0.3 | <2 | <0.3
Cl- | mg/kg |  | <0.5 | 
Fe | mg/kg | <0.02 |  | 
Cu (za NTO) | μg/kg |  |  | <3
O2 | mg/kg | <0.01 |  | <0.03 před dávk.N2H4
N2H4 | mg/kg | 0,02-0,06 |  | 
oil | mg/kg |  |  | <0.1
activity | Bq/kg |  | 370 | 
Table 8. Example of chemical regime of secondary loop of unit PWR (VVER 440) with brass condensors

## Slide 5
 | Obligatory limits | Recommended limits
conductivity | <2000 μS/cm | 
m | <3 mval/l | 
SO42- | <500 mg/l | 
Cl- | <500 mg/l | 
pH |  | >6
Ion dissolved substances |  | < 20 mmol/l
Mg |  | <200 mg/l
CHSK |  | <30 mg O2 / l
NO3 |  | <50 mg/l
NH3 |  | < 2 mg/l
Non dissolved subst. |  | <200 mg/l *
Fe |  | <3 mg/l
agressive CO2 |  | <7 mg/l
Oil products |  | <1 mg/l *
Cl- | < 230 mg/l
Non-dissolved substances | < 30 mg/l
Oil products | < 0.5 mg/l
Example of chemical regime for cooling loop (third loop), unit PWR (WWER 440) with brass condensors
(these limits are controlled by administrative authority of the state) specific values could be following

## Slide 6
KOH | 140 g/kg
H3BO3 | 150 g/kg
N2H4.H2O | 10 g/kg
Solution for safety system – (shower system)